## QC Issues
ID | Tier | Severity | Type | Disciplines | Sheets | Potential discrepancy | Evidence | Method | Confidence | Why this tier | Status | Reviewer | Reviewer comment
F-001 | confirmed | high | cross discipline conflict | M | M-601 | Potential discrepancy: EF-1 requires 120/1 power (M-601) but no branch circuit serves it on the panel schedules. | [CD_Set_RevB.pdf M-601 p6] equipment row: "EF-1" [CD_Set_RevB.pdf M-601 p6] required power: "120/1" | rule:XD-002 | 0.9 | Checked against every panel schedule in the set. | Open
F-002 | confirmed | high | cross discipline conflict | M, S | M-601, S-101 | Potential discrepancy: RTU-1 operating weight 2,450 LB (M-601) exceeds the 2,000 LB design weight on S-101. | [CD_Set_RevB.pdf M-601 p6] equipment weight: "2,450" [CD_Set_RevB.pdf S-101 p4] structural design weight: "RTU-1: DESIGN MAX OPERATING WEIGHT 2,000 LB" | rule:XD-004 | 0.95 |  | Open
F-003 | confirmed | high | cross discipline conflict | E, M | E-601, M-601 | Potential discrepancy: RTU-2 is scheduled 460/3 on M-601 but is fed 208/3 from panel LA ckt 7,9,11 on E-601. | [CD_Set_RevB.pdf M-601 p6] mechanical V/PH: "460/3" [CD_Set_RevB.pdf E-601 p7] electrical V/PH: "208/3" [CD_Set_RevB.pdf E-601 p7] panel load: "RTU-2" | rule:XD-001 | 0.95 |  | Open
F-004 | confirmed | high | cross discipline conflict | E, M | E-601, M-601 | Potential discrepancy: RTU-3 MCA 30 A (M-601) exceeds the 15 A breaker on panel HA ckt 13,15,17 (E-601). | [CD_Set_RevB.pdf M-601 p6] MCA: "30" [CD_Set_RevB.pdf E-601 p7] breaker: "15" [CD_Set_RevB.pdf E-601 p7] panel load: "RTU-3" | rule:XD-003 | 0.95 |  | Open
F-005 | confirmed | high | dimension conflict | A, S | A-101, S-101 | Potential discrepancy: grid 1-2 is dimensioned differently across sheets: A-101 = 24'-6"; S-101 = 25'-0". | [CD_Set_RevB.pdf A-101 p2] grid dimension: "24'-6"" [CD_Set_RevB.pdf S-101 p4] grid dimension: "25'-0"" | rule:DIM-003 | 0.95 |  | Open
F-006 | confirmed | high | dimension conflict | A | A-101 | Potential discrepancy on A-101: chained dimensions 24'-6" + 30'-0" + 25'-0" = 79'-6", but the overall dimension (grid 1-4) reads 80'-0". | [CD_Set_RevB.pdf A-101 p2] overall dimension: "80'-0"" [CD_Set_RevB.pdf A-101 p2] chain dimension: "24'-6"" [CD_Set_RevB.pdf A-101 p2] chain dimension: "30'-0"" [CD_Set_RevB.pdf A-101 p2] chain dimension: "25'-0"" | rule:DIM-001 | 0.97 |  | Open
F-007 | confirmed | high | dimension conflict | S | S-101 | Potential discrepancy on S-101: chained dimensions 25'-0" + 32'-0" + 25'-0" = 82'-0", but the overall dimension (grid 1-4) reads 80'-0". | [CD_Set_RevB.pdf S-101 p4] overall dimension: "80'-0"" [CD_Set_RevB.pdf S-101 p4] chain dimension: "25'-0"" [CD_Set_RevB.pdf S-101 p4] chain dimension: "32'-0"" [CD_Set_RevB.pdf S-101 p4] chain dimension: "25'-0"" | rule:DIM-001 | 0.97 |  | Open
F-008 | confirmed | high | dimension conflict | A, S | A-101, S-101 | Potential discrepancy: grid 2-3 is dimensioned differently across sheets: A-101 = 30'-0"; S-101 = 32'-0". | [CD_Set_RevB.pdf A-101 p2] grid dimension: "30'-0"" [CD_Set_RevB.pdf S-101 p4] grid dimension: "32'-0"" | rule:DIM-003 | 0.95 |  | Open
F-009 | confirmed | high | quantity mismatch | A | A-601, BOQ | Potential discrepancy: door type D1: 9 door(s) in the schedule (101, 102, 103, 104, 105, 106, 108A, 110, 122); BOQ 08-100 = 8 EA. | [BOQ_RevB.xlsx BOQ!E6] BOQ quantity: "8" [CD_Set_RevB.pdf A-601 p3] schedule row: "D1" [CD_Set_RevB.pdf A-601 p3] schedule row: "D1" | rule:QTY-001 | 0.95 | Counts schedule rows per door type; plan-vs-schedule differences are reported separately as undefined/orphan tags. | Open
F-010 | confirmed | high | quantity mismatch | A | A-601, BOQ | Potential discrepancy: door type D2: 3 door(s) in the schedule (107, 108, 109); BOQ 08-110 = 2 EA. | [BOQ_RevB.xlsx BOQ!E7] BOQ quantity: "2" [CD_Set_RevB.pdf A-601 p3] schedule row: "D2" [CD_Set_RevB.pdf A-601 p3] schedule row: "D2" | rule:QTY-001 | 0.95 | Counts schedule rows per door type; plan-vs-schedule differences are reported separately as undefined/orphan tags. | Open
F-011 | confirmed | high | quantity mismatch | M | BOQ, M-601 | Potential discrepancy: EF-1: schedule M-601 QTY = 1, BOQ 23-130 = 2 EA. | [CD_Set_RevB.pdf M-601 p6] schedule quantity: "1" [BOQ_RevB.xlsx BOQ!E14] BOQ quantity: "2" | rule:QTY-002 | 0.95 |  | Open
F-012 | confirmed | high | revision issue | A | A-601 | Potential discrepancy: A-601 changed between Rev A and Rev B without a revision cloud: '3'-0"' -> '3'-6"' (WIDTH). | [CD_Set_RevB.pdf A-601 p3] Rev B content: "3'-6"" [CD_Set_RevA.pdf A-601 p3] Rev A content: "3'-0"" | rule:REV-001 | 0.95 | Unclouded changes are easy to miss in bid/addendum review; confirm the change is intended and cloud it, or revert it. | Open
F-013 | probable | high | spec conflict | A | A-601 | Potential discrepancy: door 101 is scheduled 90 MIN but Section 08 14 16 permits 20, 45, 60 minute ratings for this door type. | [CD_Set_RevB.pdf A-601 p3] schedule fire rating: "90 MIN" [Project_Manual.pdf 08 14 16 p2] spec permitted ratings: "rated 20, 45 and 60 minutes" [Project_Manual.pdf 08 14 16 p2] spec restriction: "Wood doors rated more than 60 minutes are not permitted; use hollow metal doors." | rule:SPEC-002 | 0.85 |  | Open
F-014 | probable | high | spec conflict | A | A-601 | Potential discrepancy: door 104 is governed by Section 08 14 16 (FLUSH WOOD DOORS) but its scheduled material is HM. | [CD_Set_RevB.pdf A-601 p3] schedule material: "HM" [CD_Set_RevB.pdf A-601 p3] schedule spec ref: "08 14 16" [Project_Manual.pdf 08 14 16 p2] governing spec paragraph: "solid core flush wood doors, 1-3/4 inches thick, WDMA I.S.1A Extra Heavy Duty" | rule:SPEC-001 | 0.85 | Material implied by the governing section title. | Open
F-015 | probable | high | spec conflict | M | M-601 | Potential discrepancy: RTU-1 remarks list refrigerant R-410A; Section 23 74 13 requires R-454B. | [CD_Set_RevB.pdf M-601 p6] schedule remarks: "R-410A, ECONOMIZER" [Project_Manual.pdf 23 74 13 p6] spec requirement: "Refrigerant: R-454B" | rule:SPEC-003 | 0.85 |  | Open
F-016 | confirmed | medium | missing info | A | A-601 | Potential discrepancy: door 102 on A-601 has no value for HDW SET (non-rated / not applicable is shown as '-', blank means missing). | [CD_Set_RevB.pdf A-601 p3] schedule row: "102" [CD_Set_RevB.pdf A-601 p3] blank HDW SET: "" | rule:MISS-003 | 0.95 |  | Open
F-017 | confirmed | medium | missing info | A | A-601 | Potential discrepancy: door 105 calls for hardware set HW-9, which is not defined in Section 08 71 00 (defined: HW-1, HW-2, HW-3, HW-4). | [CD_Set_RevB.pdf A-601 p3] schedule hardware set: "HW-9" [Project_Manual.pdf 08 71 00 p3] spec section: "SECTION 08 71 00" | rule:MISS-004 | 0.95 |  | Open
F-018 | confirmed | medium | missing info | A | A-101 | Potential discrepancy: door tag 121 on A-101 has no row in the door schedule (A-601). | [CD_Set_RevB.pdf A-101 p2] plan tag: "121" | rule:MISS-001 | 0.95 | Every door tag on a plan should resolve to exactly one schedule row. | Open
F-019 | confirmed | medium | missing info | M | M-101 | Potential discrepancy: equipment tag EF-4 on M-101 is not in the equipment schedule (M-601). | [CD_Set_RevB.pdf M-101 p5] plan tag: "EF-4" | rule:MISS-009 | 0.95 |  | Open
F-020 | confirmed | medium | missing info | A, G | A-101, G-001 | Potential discrepancy: sheet A-501 is referenced/listed but is not included in the drawing set. | [CD_Set_RevB.pdf A-101 p2] sheet reference: "A-501" [CD_Set_RevB.pdf G-001 p1] sheet index: "A-501" | rule:MISS-006 | 0.95 |  | Open
F-021 | confirmed | medium | missing info | A | A-601, BOQ | Potential discrepancy: Section 08 41 13 is referenced 4 time(s) (schedules / BOQ / notes) but is not included in the project manual. | [CD_Set_RevB.pdf A-601 p3] door schedule: "08 41 13" [CD_Set_RevB.pdf A-601 p3] door schedule: "08 41 13" [CD_Set_RevB.pdf A-601 p3] drawing note: "SEE SECTION 08 41 13" [BOQ_RevB.xlsx BOQ!C8] BOQ line: "08 41 13" | rule:MISS-005 | 0.95 |  | Open
F-022 | confirmed | medium | quantity mismatch | M | BOQ, M-101, M-601 | Potential discrepancy: EF-3 is marked NIC (not in contract) but BOQ 23-150 prices 1 EA. | [BOQ_RevB.xlsx BOQ!E16] BOQ quantity: "1" [CD_Set_RevB.pdf M-601 p6] schedule remarks: "NIC - BY OWNER" [CD_Set_RevB.pdf M-101 p5] plan NIC note: "(NIC)" | rule:QTY-003 | 0.95 |  | Open
F-023 | confirmed | medium | revision issue | M | M-601 | Potential discrepancy: M-601 content changed (1 change(s)) but its title block still shows Rev A; the revision was not issued on this sheet. | [CD_Set_RevB.pdf M-601 p6] latest revision in title block: "A" [CD_Set_RevB.pdf M-601 p6] changed content: "12.5 TON" | rule:REV-002 | 0.9 |  | Open
F-024 | confirmed | medium | tag conflict | A | A-101 | Potential discrepancy: door number 107 is tagged 2 times on the plans; door numbers must be unique. | [CD_Set_RevB.pdf A-101 p2] plan tag: "107" [CD_Set_RevB.pdf A-101 p2] plan tag: "107" | rule:TAG-001 | 0.95 |  | Open
F-025 | probable | medium | dimension conflict | A | A-101 | Potential discrepancy on A-101: dimension text 24'-6" (grid 1-2) but the drawn length measures about 25'-0" at 1/8" = 1'-0". Possible overridden dimension. | [CD_Set_RevB.pdf A-101 p2] dimension text: "24'-6"" | rule:DIM-002 | 0.75 | Probable only: drawings say DO NOT SCALE and some views are not to scale; the text may be right and the graphics wrong, or vice versa. | Open
F-026 | probable | medium | dimension conflict | S | S-101 | Potential discrepancy on S-101: dimension text 32'-0" (grid 2-3) but the drawn length measures about 30'-0" at 1/8" = 1'-0". Possible overridden dimension. | [CD_Set_RevB.pdf S-101 p4] dimension text: "32'-0"" | rule:DIM-002 | 0.75 | Probable only: drawings say DO NOT SCALE and some views are not to scale; the text may be right and the graphics wrong, or vice versa. | Open
F-027 | confirmed | low | missing info | G, S | G-001, S-101 | Potential discrepancy: sheet S-101 is in the set but missing from the sheet index on G-001. | [CD_Set_RevB.pdf S-101 p4] title block sheet number: "S-101" [CD_Set_RevB.pdf G-001 p1] sheet index (last entry): "E-601" | rule:MISS-007 | 0.9 |  | Open
F-028 | probable | low | missing info | A | A-601 | Potential discrepancy: door 108 is scheduled on A-601 but is not tagged on any plan in this set. | [CD_Set_RevB.pdf A-601 p3] schedule row: "108" | rule:MISS-002 | 0.85 | Probable rather than confirmed: the door may be on a plan sheet that is not part of this set. | Open
F-029 | probable | low | missing info | A | A-601 | Potential discrepancy: door 122 is scheduled on A-601 but is not tagged on any plan in this set. | [CD_Set_RevB.pdf A-601 p3] schedule row: "122" | rule:MISS-002 | 0.85 | Probable rather than confirmed: the door may be on a plan sheet that is not part of this set. | Open
F-030 | needs_review | low | quantity mismatch | M | M-101, M-601 | Plan quantity for VAV-2 cannot be determined from the sheet: tag is marked 'TYP.' without a count. Schedule QTY = 3, BOQ = 3. Reviewer to confirm the count. | [CD_Set_RevB.pdf M-101 p5] plan tag: "VAV-2" [CD_Set_RevB.pdf M-101 p5] TYP. note: "TYP." [CD_Set_RevB.pdf M-601 p6] schedule quantity: "3" | rule:QTY-004 | 0.5 | Abstained: 'TYP.' means the element repeats, but the sheet does not say how many times. | Open

## Run summary
Metric | Value
sheets | 7
spec_sections | 6
boq_items | 12
door_tags | 14
door_rows | 14
equipment_tags | 9
equipment_rows | 8
dimensions | 14
graph_edges | 102
revision_changes | 5
findings | 30
needs_review | 1
rejected_by_gate | 0
anchors_checked | 68
anchors_verified | 68
seconds | 1.02
ingest_seconds | 0.68
Note | All findings are potential discrepancies for engineer review. The tool does not approve, seal or modify drawings; the AOR/EOR decides.